| Fume Cabinet Inspection Checklist |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Checklist Item |  | Yes | No | Notes and observations |  |
| Thorough Examination and Test completed within the previous 14-month period |  |  |  |  |  |
| Any signs of physical damage to the cabinet (internal or external) |  |  |  |  |  |
| Cracking, damage or degradation of the sealant at the edges of the cabinet |  |  |  |  |  |
| Sash moves smoothly through full range and remains in position when released |  |  |  |  |  |
| Fume cupboard sash clear and not obscured with writing or signs. |  |  |  |  |  |
| Alarm is operational (visual and audible) when sash raised above safety point |  |  |  |  |  |
| Sash high position restrictor in place and functioning properly |  |  |  |  |  |
| Air flow reading indicator present and working correctly (note air flow reading) |  |  |  |  |  |
| Cabinet lights (where present) are functioning |  |  |  |  |  |
| Water supply to cabinet (where present) working and flushed for 2 minutes. |  |  |  |  |  |
| Gas supply (where present) operational with no evidence of leakage |  |  |  |  |  |
| Recirculating filter present and changed within supplier guidelines |  |  |  |  |  |
| Visible ductwork associated with cabinet in good condition with no obvious breaches |  |  |  |  |  |
| Good housekeeping with no restriction to air flow at the rear of the workspace |  |  |  |  |  |
| Surfaces reasonably clean and free of contamination |  |  |  |  |  |
| Debris or detritus present on the ventilation grille / baffles at rear of the cabinet |  |  |  |  |  |
| Secondary containment of waste containers and other stored liquids |  |  |  |  |  |
| Fume Hood Location |  |  | Fume Hood Reference |  |  |
| Inspector Name |  |  | Date of Inspection |  |  |